## GenTest Procedures
| SBC Project No: | [5 empty] | Page |  | of
| Institution or Campus: | [5 empty] | Date:
Building: | [6 empty] | Tests
Installer: | [6 empty] | run by:
|  | Manufacturer: |  |  |  | Model:
Location: | [5 empty] | Serial No:
Step by Step Detailed Procedure |  |  | Expected Result |  |  |  |  | Observations
1. ATS Breaker |  | Open ATS Breaker | Verify power off at all loads on emergency power.
|  | Close ATS Breaker & put ATS Sw. to Auto | Verify all loads have power.
2. Generator Cold |  | Open normal power breaker & immediately | Time delay from power failure to engin start should be
Start |  | connect full load bank load capacity to ATS | within sec.
|  | units. (This connection must be made | Cranking time until prime mover starts and runs should
|  | before the generator engine is up to speed | be within sec.
|  | & transfer to emergency power is complete. | Time until engine-generator is at proper voltage and
|  | Observe the systems performance & record | frequency should be within sec.
|  | the date using a Power Line Disturbance | Total time from power failure until ATS switch is on
|  | Monitor to monitor transient responses. | emergency power should be within sec.
Compare to specifications.
3. Repeat Generator |  | Open normal power breaker & immediately | Time delay from power failure to engin start should be
Cold Start |  | connect full load bank load capacity to ATS | within sec.
|  | units. (This connection must be made | Cranking time until prime mover starts and runs should
|  | before the generator engine is up to speed | be within sec.
|  | & transfer to emergency power is complete. | Time until engine-generator is at proper voltage and
|  | Observe the systems performance & record | frequency should be within sec.
|  | the date using a Power Line Disturbance | Total time from power failure until ATS switch is on
|  | Monitor to monitor transient responses. | emergency power should be within sec.
Compare to specifications.
4. Phase Testing |  | Record voltage & amperage of each phase | Voltage |  |  |  | V
|  | & frequency using analyzer, not generator | Frequency |  |  |  | HZ
|  | gages; engine temperature, oil pressure & | Amperage |  |  |  | A
|  | battery charge rate at 5 minute intervals for | Coolant Temp. |  |  |  | F
|  | a period of one hour. Measure the temp. of | Oil Pressure |  |  |  | PSI
|  | all generator & ATS connections using a | Battery Charge Rate
|  | laser guided infrared temperature meter. | ATS Contacts Input Temp. |  |  |  | F
|  |  | ATS Contacts Onput Temp. |  |  |  | F
ABOVE VALUES PERFORMANCE CRITERIA FOR
TABLE IN SECTION 26 08 32
5. Return to Normal |  | Disconnect Load Bank from ATS, before
Power |  | transfer back to normal power. | Time delay to return normal power should be within
|  | Restore Normal Power Breaker and record | sec.
|  | delay to normal power transfer using PDM. | Neutral delay time should be within sec.
|  | Record neutral delay time by recording V | Generator Power to Utility Power, V should be 0.
differential between EGP & UP at the time
|  | of the transfer back to normal power using | Engine continues to run & cool down time should be
|  | PDM. | min.
6. Step Load |  | After cool-down timer has expired, start the | Step | Voltage | FrequencyFrequency Stability
Testing |  | generator by opening the ATS normal input | Specified | V | HZ | Criteria
|  | power breaker. With the emergency bus | 0-25% | V | HZ
|  | energized perform the step load test verify | 0-50% | V | HZ
|  | that volts & HZ stay within specified range | 0-100% | V | HZ
|  | during transition & HZ stability (rate of | 100-50% | V | HZ
|  | change) is acceptable using PDM. | 100-25% | V | HZ
7. Temperature on |  | Connect full load bank to ATS
Load Bank |  |  | There should be no significant diff in temp between Phs
|  | Maintain power flow for 15 min and then | Phase 1 |  | Phase 2 |  | Phase 3
|  | take temperature readings with infrared | F |  | F |  | F
|  | meter looking for hot spots. | F |  | F |  | F
8. Temperature on |  | Transfer load to Utility source
Utility |  |  | There should be no significant diff in temp between Phs
|  | Maintain power flow fro 15 min and then | Phase 1 |  | Phase 2 |  | Phase 3
|  | take temperature readings with infrared | F |  | F |  | F
|  | meter looking for hot spots. | F |  | F |  | F
9. ATS Test Switch |  | Operate the ATS test switch & verify that | Generator should start and emergency power sequence
|  | generator starts and emergency power | initiate. Verify that total time to emergency power meets
|  | sequence is initiated. | that specified (see procedure 2)
Bypass the return to normal timer to
accelerate the test sequence.
10. Safety Interlocks |  | Operate the ATS and controls in a deranged | Alarms should be generated and emergency power
ATS |  | mannet to create an alarm condition | remains off.
11. Alarms ATS |  | Simulate all alarms, alarm contact operation | All alarms are properly annunciated in the remote panel
and remote enunciator operation by
jumping across alarms
12. ATS Digital |  | Check calibration of ATS digital readouts of | ATS should be within tolerances
Readouts |  | frequency, current and volts against a |  |  | Specified |  | Actual
|  | calibrated instrument. | Voltage |  | V |  | V
|  |  | Ampereage |  | A |  | A
|  |  | Frequency |  | HZ |  | HZ
13. UPS with Load |  | Connect the UPS to a load bank and leave | UPS values should be within tolereances
Bank Off |  | the load bank off. Operate the UPS for 1/2 |  |  | Specified |  | Actual
|  | hour without load while monitoring UPS | Voltage |  | V |  | V
|  | output with Power Line Disturbance | Frequency |  | HZ |  | HZ
|  | Monitor and Load Profiler. Take a waveform | THD |  | < 5% |  | %
|  | and load profiler snapshot. Observe the | Waveform |  | Minimal
|  | varations in voltage, frequency, total | Deviation
harmonic distortion (THD), and the wave
form deviation.
14. UPS with Load |  | Bring the UPS to its 50% kW rating | UPS values should be within tolereances
Bank at 50% |  | (balanced load) in 25% increments. Operate |  |  | Specified |  | Actual
|  | the UPS for 1 hour and monitor UPS output | Voltage |  | V |  | V
|  |  | Frequency |  | HZ |  | HZ
|  |  | THD |  | < 5% |  | %
|  |  | Waveform |  | Minimal
Deviation
15. UPS with Load |  | Bring load bank load up to 100% of rated | UPS values should be within tolereances
Bank at 100% |  | kW (balanced load) and monitor UPS |  |  | Specified |  | Actual
|  | output for 2 continuous hours. | Voltage |  | V |  | V
|  |  | Frequency |  | HZ |  | HZ
|  |  | THD |  | < 5% |  | %
|  |  | Waveform |  | Minimal
Deviation
|  | Record all electrical distribution systems | There should be no significant diff in temp between Phs
|  | connection temperatures using an infrared | Phase 1 |  | Phase 2 |  | Phase 3
|  | meter. | F |  | F |  | F
|  |  | F |  | F |  | F
16. UPS Step Load |  | Monitor and record the UPS performance | Step | VO, V | FO, HZ | THD, % | Wave
Test |  | for Voltage Overshoot (VO), Frequency | Specified |  |  | < 5.0 | Minimal
UPS shall be |  | Overshoot (FO), Total Harmonic | 0%/15sec
subjected to 3 |  | Distortion (THD) and Waveform Deviation. | 25%/15sec
consecutive step |  | The generator should power load and not | 0%/15sce
load tests. |  | transfer to battery. | 50%/15sec
|  | The UPS will be monitored and waveform | 0%/15sec
|  | deformation/harmonic content. Each of the | 100%/15sec
|  | four step tests shall be performed at 1 min. | 50%/15sec
|  | intervals until 3 repitions have been | 100%/15sec
|  | completed. | 50%/15sec
(16. ups Step Load test continued on next page) |  |  | 125%/15sec
(16. ups Step Load test continued from previous page) |  |  | Step | VO, V | FO, HZ | THD, % | Wave
UPS shall be |  | Monitor and record the UPS performance | Specified |  |  | < 5.0 | Minimal
subjected to 3 |  | for Voltage Overshoot (VO), Frequency | 0%/15sec
consecutive step |  | Overshoot (FO), Total Harmonic | 25%/15sec
load tests. |  | Distortion (THD) and Waveform Deviation. | 0%/15sce
|  | The generator should power load and not | 50%/15sec
|  | transfer to battery. | 0%/15sec
|  | The UPS will be monitored and waveform | 100%/15sec
|  | deformation/harmonic content. Each of the | 50%/15sec
|  | four step tests shall be performed at 1 min. | 100%/15sec
|  | intervals until 3 repitions have been | 50%/15sec
|  | completed. | 125%/15sec
0%/15sec
25%/15sec
0%/15sce
50%/15sec
0%/15sec
100%/15sec
50%/15sec
100%/15sec
50%/15sec
125%/15sec
100%/5min
125%/5min
17. Grounding |  | Verify connections & grounding is in | Wiring & grounding are in compliance with NEC.
compliance with NEC, especicially
grounding & bonding of UPS & generator.
18. UPS with Load |  | With the UPA loaded as stated in the | UPS values should be within the following .
Bank at 100% |  | previous test, the UPS INTERNAL manual |  |  | Specified |  | Actural
|  | maintenance bypass switch will be manually | Voltage
|  | operated 2 consecutive times transferring | Frequency
|  | the load between UPS power, alternate | THD
|  | power, and back to UPS power. Switching | Waveform
|  | shall occur in 2 minute intervals. Verify | Deviation
that specified voltage dynamic regulation
is met during switching.
19. UPS with Load |  | With the UPA loaded as stated in the | UPS values should be within the following .
Bank at 100% |  | previous test, the UPS EXTERNAL manual |  |  | Specified |  | Actural
|  | maintenance bypass switch will be manually | Voltage
|  | operated 2 consecutive times transferring | Frequency
|  | the load between UPS power, alternate | THD
|  | power, and back to UPS power. Switching | Waveform
|  | shall occur in 2 minute intervals. Verify | Deviation
that specified voltage dynamic regulation
is met during switching.
20. Safety Interlocks |  | Operate the UPS & controls in a deranged | Alarms should be generated and emergency power
UPS |  | manner to create alarm condition. | will remain off.
21. Alarms UPS |  | Simulate all alarms, alarm contact operation | All alarms are properly annunciated at the remote panel.
and remote enunciation operation by
jumping across alarms.
22. UPS Digital |  | Check calibration of UPS digital readouts | UPS should be within tolerances
Readouts |  | of frequency, current and volts against a |  |  | Specified |  | Actual
|  | calibrated instrument. | Voltage |  | V |  | V
|  |  | Ampereage |  | A |  | A
|  |  | Frequency |  | HZ |  | HZ
23. UPS with Load |  | With the UPS loaded at 100%, UPS input | UPS values should be within these tollerances.
Bank at 100% |  | power will be interrupted to simulate a power |  |  | Specified |  | Actual
|  | failure. The UPS output will be monitored & | RMS |  | V |  | V
|  | recorded for RMS values, waveform | Battery |  | A/sec |  | A/sec
|  | deformation/harmonic content. The roll-off | THD |  | < 5%
|  | of battery potential shall be monitored, | Waveform |  | Minimal
|  | recorded and compared to the battery run | Deviation
|  | time spec. All accessible battery | UPS shutdown at
|  | terminations will be checked for temperature | low battery string volts |  | V |  | V
variations with a infrared meter.
24. Preparation |  | Reconnect power to the UPS and with
Integrated Building |  | 100% output load on the UPS system and
Test |  | full battery recharged current (waite aprox.
5 minutes to allow batteries to charge to
support load during loss of power).
25.Emergency Power |  | Test the function of all loads on emergency | Generator values should be within following tolerances.
Including UPS |  | power including UPS loads. |  |  | Specified |  | Actural
|  | Open the circuit breaker serving the ATS to | Load |  | < 100% |  | %
|  | simulate a power failure on the feeder | UPS loads should properly operate off the generator
|  | serving the ATS & Backup Power | and not transfer to battery.
Distribution System.
|  | Verify that proper power is delivered to each | All emergency lights ON.
|  | device listed in the emergency panel | All emergency receptacles powered.
|  | schedules and that equipment directly wired | Fire Alarm system powered.
|  | function properly. Record generator output | Specialty systems powered.
|  | with the Powerline Disturbance Monitor | HVAC & Controls powered.
and a Load Profiler.
26.Emergency Power |  | Initiate a building smoke detector. | Fire alarm should work properly.
Specialty System |  | Initiate a security system alarm. | Security system should work properly
Test |  | Initiate a HVAC alarm. | HVAC monitoring system should work properly.
|  | Check telecom system. | Telecom system works properly.
|  | Test elevator recall. | Elevator works properly.
|  | Monitor UPS charging system | UPS charging properly.
SYSTEM THAT HAVE OFF SITE MONITORING
VERIFY THAT CORRECT SIGNALS ARE SENT
AND RECEIVED.
27 Emergency Power |  | Verify the following functions by causing
Including UPS |  | the alarm, recording the time and having
Monitored Alarms |  | the monitoring company fax a copy of the
alarm condition.
|  | Simulate an electrical failure or malfunction | Electrical failure alarm.
Response Time:
|  | Simulate a UPS switch detection. | Power switched alarm.
Response Time:
|  | Simulate a HVAC condition alarm. | HVAC alarm.
Response Time: